## Sheet1
LSIS VFD Common Modbus RTU Communications Address's
Comm. Address (Register) | With Decremented Offset | Parameter | Scale | Unit | R/W | Assigned Content by Bit
40000 |  | Inverter model | - | - | R | 6: S100
40001 | 40000 | Inverter capacity | - | - | R | 0: 0.75 kW, 1: 1.5 kW, 2: 2.2 kW 3: 3.7 kW, 4: 5.5 kW, 5: 7.5 kW … Range varies by drive series
40002 | 40001 | Inverter input voltage | - | - | R | 0: 200V product
1: 400V product
40003 | 40002 | Version | - | - | R | Example 0h0100: Version 1.00
Example 0h0101: Version 1.01
40004 | 40003 | Reserved | - | - | R/W
40005 | 40004 | Command frequency | 0.01 | Hz | R/W
40006 | 40005 | Operation command (option) | - | - | R | B15 | Reserved
[6 empty] | B14 | 0: Keypad Freq, 1: Keypad Torq 2-16: Terminal block multi- step speed 17: Up, 18: Down 19: STEADY 22: V1, 24: V2, 25: I2, 26: Reserved 27: Built-in 485 28: Communication option 30: JOG, 31: PID
B13
B12
B11
B10
B9
[6 empty] | B8 | 0: Keypad 1: Fx/Rx-1 2: Fx/Rx-2 3: Built-in 485 4: Communication option
B7
B6
[5 empty] | R/W | B5 | Reserved
[6 empty] | B4 | Emergency stop
[6 empty] | B3 | W: Trip initialization (01), R: Trip status
[6 empty] | B2 | Reverse operation (R)
[6 empty] | B1 | Forward operation (F)
[6 empty] | B0 | Stop (S)
40007 | 40006 | Acceleration time | 0.1 | s | R/W | -
40008 | 40007 | Deceleration time | 0.1 | s | R/W | -
40009 | 40008 | Output current | 0.1 | A | R | -
40010 | 40009 | Output frequency | 0.01 | Hz | R | -
40011 | 40010 | Output voltage | 1 | V | R | -
40012 | 40011 | DC link voltage | 1 | V | R | -
40013 | 40012 | Output power | 0.1 | kW | R | -
40014 | 40013 | Operation status | - | - | R | B15 | 0: Remote, 1: Keypad Local
[6 empty] | B14 | 1: Frequency command source by communication (built-in, option)
[6 empty] | B13 | 1: Operation command source by communication (built-in, option)
[6 empty] | B12 | Reverse operation command
[6 empty] | B11 | Forward operation command
[6 empty] | B10 | Brake release signal
[6 empty] | B9 | Jog mode
[6 empty] | B8 | Drive stopped.
[6 empty] | B7 | DC Braking
[6 empty] | B6 | Speed reached
[6 empty] | B5 | Decelerating
[6 empty] | B4 | Accelerating
[6 empty] | B3 | Fault Trip - operates according to Pr.30 setting
[6 empty] | B2 | Operating in reverse direction
[6 empty] | B1 | Operating in forward direction
[6 empty] | B0 | Stopped
40015 | 40014 | Fault trip information | - | - | R | B15 | Reserved
[6 empty] | B14 | Reserved
[6 empty] | B13 | Reserved
[6 empty] | B12 | Reserved
[6 empty] | B11 | Reserved
[6 empty] | B10 | H/W-Diag
[6 empty] | B9 | Reserved
[6 empty] | B8 | Reserved
[6 empty] | B7 | Reserved
[6 empty] | B6 | Reserved
[6 empty] | B5 | Reserved
[6 empty] | B4 | Reserved
[6 empty] | B3 | Level Type trip
[6 empty] | B2 | Reserved
[6 empty] | B1 | Reserved
[6 empty] | B0 | Latch Type trip
40016 | 40015 | Input terminal information | - | - | R | B15- B7 | Reserved
[6 empty] | B6 | P7
[6 empty] | B5 | P6
[6 empty] | B4 | P5
[6 empty] | B3 | P4
[6 empty] | B2 | P3
[6 empty] | B1 | P2
[6 empty] | B0 | P1
40017 | 40016 | Output terminal information | - | - | R | B15 | Reserved
[6 empty] | B14 | Reserved
[6 empty] | B13 | Reserved
[6 empty] | B12 | Reserved
[6 empty] | B11 | Reserved
[6 empty] | B10 | Reserved
[6 empty] | B9 | Reserved
[6 empty] | B8 | Reserved
[6 empty] | B7 | Reserved
[6 empty] | B6 | Reserved
[6 empty] | B5 | Reserved
[6 empty] | B4 | Reserved
[6 empty] | B3 | Reserved
[6 empty] | B2 | Reserved
[6 empty] | B1 | MO
[6 empty] | B0 | Relay 1
40018 | 40017 | V1 | 0.01 | % | R | V1 input voltage
40019 | 40018 | V2 | 0.01 | % | R | V2 input voltage
40020 | 40019 | I2 | 0.01 | % | R | I2 input current
40021 | 40020 | Motor rotation speed | 1 | rpm | R | Displays existing motor rotation speed
40022 | 40021 | Reserved | - | - | - | -
40023 | 40022 | Select Hz/rpm | - | - | R | 0: Hz unit, 1: rpm unit
40024 | 40023 | Display the number of poles for the selected motor | - | - | R | Display the number of poles for the selected motor
Rev B